## Slide 1: IEEE 39 Bus Contingency Analysis

## Slide 2: System Information
Total generation: 6167.33 MW
Max Capacity: 6779.24 MW
  Reduced generator Max MW to 112% of generator output for non-solar generators
    Assuming that solar generators cannot increase their MW output
Capacity left: 611.91 MW
Total load: 6124.5 MW

## Slide 3: Total Generation vs Max Capacity
Pre-Contingency Total Generation = 6167.33 MW |  |  | 
Tripped Generator | Max MW Capacity | Total Gen < Max MW | Capacity Left MW
30 | 6499.24 | √ | 331.91
31 | 6166.24 | x | 
32 | 6051.24 | x | 
33 | 6071.4 | x | 
34 | ------------- solar | ------------- solar | 
35 | 6051.24 | x | 
36 | ------------- solar | ------------- solar | 
37 | 6174.44 | √ | 7.11
38 | 5849.64 | x | 
39 | ------------- FO Target | ------------- FO Target | 

## Slide 4: Load Relay Setting
Referencing WECC’s Off-Nominal Frequency Load Shedding Plan [1]
  “Under frequency relays must have a max operating time of 6 cycles (0.1s) for high speed trip”
  “System average operating time of breakers used to trip load is to be no more than 14 cycles (0.23s)”
Set Stage 1 frequency pick up: 59 Hz
  Pickup time: 6 cycles (0.1s)
  Breaker time: 3 cycles (0.05s)
  Shed 10% of total load
    0.1* 6124.5 = 612.45 MW
[1] https://www.wecc.org/Reliability/Off-Nominal%20Frequency%20Load%20Shedding%20Plan.pdf

## Slide 5: Trip Gen 37 Only
Trip Gen 37 @ 10s
Lowest frequency occurs at approximately 23s
  Increase total load around this time to further drop the frequency
Min Freq
Contingency: Trip Gen 37

## Slide 6: Contingency 1: Gen Trip and Load Increase Event

## Slide 7: Contingency 1
Contingency:
  Trip Gen 37 @ 10s
    540 MW output generation disconnected
    Pre-contingency max capacity decreased by 604.8 MW
  Increase Load 39 by 25 MW @ 20s
Ideally:
  Total generation > Max capacity
  Recall: ~7 MW capacity left post generator contingency
However, there is an issue with how Power World does its transient analysis calculations

## Slide 8: Power World Calculation Issue
Load 39 does increase by 25 MW, however, there is a decrease in the rest of the loads
Results:
Total generation decreased by 8.4855 MW
Total load decreased by 10.6525 MW
Solution: Increase Load 39 until total generation > max capacity
  Increase load 39 by 50 MW or more
 | Pre-Contingency MW | Post-Contingency MW | Difference: Post - Pre
Generation | 6167.3274 | 6158.8419 | -8.4855
Load | 6124.5 | 6113.8475 | -10.6525

## Slide 9: New Contingency 1
Trip Gen 37 @ 10s
Increase Load 39 by 50 MW @ 20s
Results
  612.45 MW of load tripped
Contingency: Trip Gen 37 with Load Increase

## Slide 10: Contingency 1 Events
Load Relay Load Shedding Events
Contingency Event

## Slide 11: Contingency 1 Results

## Slide 12: Contingency 1 Results

## Slide 13: Contingency 1 Results

## Slide 14: Contingency 1 Results

## Slide 15: Contingency 1 Results

## Slide 16: Contingency 1 Results

## Slide 17: Returning Gen 37 Online Post Load Shedding @ 300s
Close Gen 37 @ 300s
  Set to output its pre-contingency 540 MW output
Contingency: Trip Gen 37 with Load Increase

## Slide 18: Returning Gen 37 Online Post Load Shedding @ 300s

## Slide 19: Returning Gen 37 Online Post Load Shedding @ 300s

## Slide 20: Returning Gen 37 Online Post Load Shedding @ 300s
Stable before Gen 37 is back online
Stable after Gen 37 is back online

## Slide 21: Returning Gen 37 Online Post Load Shedding @ 300s

## Slide 22: Returning Gen 37 Online Post Load Shedding @ 300s

## Slide 23: Returning Gen 37 Online Post Load Shedding @ 300s

## Slide 24: Returning Gen 37 Online Post Load Shedding @ 300s

## Slide 25: Contingency 2: Gen Trip and Load Switching FO

## Slide 26: Contingency 2: Load switching FO
Apply 0.6Hz load perturbation at Load 39 @ 2 sec
Disconnect Gen 37 @ 10 sec
Initial demand at Load 39: 1104 MW
Test 1:
  +/- 50 MW from initial load value
Test 2:
  +/- 100 MW from initial load value
Contingency: Load Switching Test 1 – 50MW
Contingency: Load Switching Test 2 – 100MW

## Slide 27: Contingency 2: Test 1 +/- 50 MW

## Slide 28: Contingency 2: Test 1 +/- 50 MW

## Slide 29: Contingency 2: Test 1 +/- 50 MW
Bus Frequency oscillates on the same trend as just tripping Gen 37 only on slide 5
Min freq > 59 Hz (load shedding freq) therefore the load relay does not trip
Min freq > 59 Hz

## Slide 30: Contingency 2: Test 1 +/- 50 MW

## Slide 31: Contingency 2: Test 1 +/- 50 MW

## Slide 32: Contingency 2: Test 1 +/- 50 MW

## Slide 33: Contingency 2: Test 1 +/- 50 MW

## Slide 34: Contingency 2: Test 2 +/- 100 MW
  From Test 1, +/- 50 MW was not enough to trigger a load shedding event
    Frequency did not drop to 59 Hz
    Total Gen Mech MW < Total turbine rated MW (rated turbine MW)
      6136 MW < 6174.44 MW
  Increase the load perturbation
    +/- 100 MW from initial load value
Contingency: Load Switching Test 2 – 100MW

## Slide 35: Contingency 2: Test 2 +/- 100 MW

## Slide 36: Contingency 2: Test 2 +/- 100 MW

## Slide 37: Contingency 2: Test 2 +/- 100 MW
Bus Frequency oscillates on the same trend as just tripping Gen 37 only on slide 5
Min freq > 59 Hz (load shedding freq) therefore the load relay does not trip
Min freq > 59 Hz

## Slide 38: Contingency 2: Test 2 +/- 100 MW

## Slide 39: Contingency 2: Test 2 +/- 100 MW

## Slide 40: Contingency 2: Test 2 +/- 100 MW

## Slide 41: Contingency 2: Test 2 +/- 100 MW

## Slide 42: Contingency 2: Test 2 +/- 100 MW
Total Gen Mech MW = 6140 MW
Total Turbine MW rating (excluding Gen 37) = 6174.44 MW
Total Gen Mech MW < Total Turbine MW
  System is stable

## Slide 43: Contingency 2: Test 3 +/- 200 MW
From Test 2, +/- 100 MW oscillation was unable to trigger load relay trip
Increase the amplitude of the FO to 200 MW
Contingency: Load Switching Test 3 – 200MW

## Slide 44: Contingency 2: Test 3 +/- 200 MW

## Slide 45: Contingency 2: Test 3 +/- 200 MW

## Slide 46: Contingency 2: Test 3 +/- 200 MW
Bus Frequency oscillates on the same trend as just tripping Gen 37 only on slide 5
Min freq > 59 Hz (load shedding freq) therefore the load relay does not trip
Min freq > 59 Hz
Bus Frequency oscillates on the same trend as just tripping Gen 37 only on slide 5
Min freq > 59 Hz (load shedding freq) therefore the load relay does not trip
Min freq > 59 Hz

## Slide 47: Contingency 2: Test 3 +/- 200 MW

## Slide 48: Contingency 2: Test 3 +/- 200 MW

## Slide 49: Contingency 2: Test 3 +/- 200 MW

## Slide 50: Contingency 2: Test 3 +/- 200 MW

## Slide 51: Contingency 2: Test 4 +/- 400 MW
From Test 2, +/- 400 MW oscillation was unable to trigger load relay trip
Increase the amplitude of the FO to 400 MW
Contingency: Load Switching Test 4 – 400MW

## Slide 52: Contingency 2: Test 4 +/- 400 MW

## Slide 53: Contingency 2: Test 4 +/- 400 MW

## Slide 54: Contingency 2: Test 4 +/- 400 MW
Bus Frequency oscillates on the same trend as just tripping Gen 37 only on slide 5
Min freq > 59 Hz (load shedding freq) therefore the load relay does not trip
Min freq > 59 Hz

## Slide 55: Contingency 2: Test 4 +/- 400 MW

## Slide 56: Contingency 2: Test 4 +/- 400 MW

## Slide 57: Contingency 2: Test 4 +/- 400 MW

## Slide 58: Contingency 2: Test 4 +/- 400 MW

## Slide 59: Contingency 2: Test 5 +/- 100 MW with bias
From Test 4, +/- 400 MW oscillation was unable to trigger load relay trip
Introduce a constant bias in addition to +/- 100 MW load switching FO
Any bias greater than 50 MW will cause the frequency to drop
100 MW bias was introduced, load relay trips @ 34.75s
  Total of 230.4 MW load was tripped
  Note: a bias of 50 MW takes longer than 125s for the frequency to drop to 59 Hz (slide 68)
Contingency: Load Switching Test 5 – 100 MW with 100 MW bias

## Slide 60: Contingency 2: Test 5 +/- 100 MW with 100 MW bias

## Slide 61: Contingency 2: Test 5 +/- 100 MW with 100 MW bias

## Slide 62: Contingency 2: Test 5 +/- 100 MW with 100 MW bias
Load Relay Trip

## Slide 63: Contingency 2: Test 5 +/- 100 MW with 100 MW bias
Zoom in of bus frequency
Shows frequency for all buses (non-load and load buses)

## Slide 64: Contingency 2: Test 5 +/- 100 MW with 100 MW bias

## Slide 65: Contingency 2: Test 5 +/- 100 MW with 100 MW bias

## Slide 66: Contingency 2: Test 5 +/- 100 MW with 100 MW bias

## Slide 67: Contingency 2: Test 5 +/- 100 MW with 100 MW bias

## Slide 68: Contingency 2: Test 5 +/- 100 MW with 50 MW bias
Contingency: Load Switching Test 5 – 100 MW with 50 MW bias