## Slide 1: IEEE 39 Bus with Solar PV

## Slide 3: Power World: Renewable Energy Generation Modeling [1]
[1] | https://www.powerworld.com/WebHelp/Content/MainDocumentation_HTML/Transient_Stability_Overview_WindModeling.htm
[2] | https://www.wecc.org/Reliability/WECC%20Solar%20Plant%20Dynamic%20Modeling%20Guidelines.pdf
Same models recommended by WECC [2]

## Slide 4: Selecting Solar PV Generators
Select the 2 smallest generators with lowest Max MW and replace with Solar PV
  Gen 30 and 37 are of interest for forced oscillation studies
  Choose Gen 34 and 36 to be Solar PV generators
Gen Ordered by Lowest to Highest Max MW

## Slide 5: Power World: SMIB Analysis
Table contains the frequency with the smallest damping ratio for each generator
Full Power World eigenvalue results are in Appendix A
Previous results with no renewable generation are in Appendix B
 | Power World SMIB |  | FO Freq Scan
Generator | Damping | Freq Hz | 
30 | 0.102 | 1.1629 | ~1.15 - 1.25 Hz
31 | 0.1683 | 1.2595 | 
32 | 0.1857 | 1.3743 | 
33 | 0.1556 | 1.5797 | 
34 | 0.8903 | 3.3909 | 
35 | 0.2208 | 1.2609 | 
36 | 0.9173 | 2.9991 | 
37 | 0.1899 | 1.7439 | ~1.75 Hz
38 | 0.2622 | 1.259 | 
39 | 0.1607 | 0.4044 | ~0.65 Hz

## Slide 6: Gen 39 Exciter Setpoint Frequency Sweep
Perturb exciter setpoint by +/- 5% rectangular pulse of starting setpoint
Perturbation frequencies:
  0.4 Hz
  0.5 Hz
  0.6 Hz
  0.7 Hz
  0.8 Hz
Contingency: Gen 39 Efd Frequency Sweep

## Slide 7: Gen 39 Exciter Setpoint Frequency Sweep
0.4 Hz
0.5 Hz
0.6 Hz
0.7 Hz
0.8 Hz
Gen_MW

## Slide 8: Gen 39 Exciter Setpoint Frequency Sweep
0.4 Hz
0.5 Hz
0.6 Hz
0.7 Hz
0.8 Hz
Gen_Efd

## Slide 9: Gen 39 Exciter Frequency Sweep Full Result

## Slide 10: Gen 39 Exciter Frequency Sweep Full Result

## Slide 11: Gen 39 Exciter Frequency Sweep Full Result

## Slide 12: Gen 39 Exciter Frequency Sweep Full Result

## Slide 13: Gen 39 Exciter Frequency Sweep Full Result

## Slide 14: Gen 39 Exciter Frequency Sweep Full Result

## Slide 15: Gen 39 Exciter Perturbation Frequency Verification
Scan resulted in a resonance frequency around ~0.7 Hz
Perturb system with frequency 0.7 +/- 0.05 Hz
Perturbation frequencies:
  0.65 Hz
  0.70 Hz
  0.75 Hz
Contingency: Gen 39 Efd Frequency Verification

## Slide 16: Gen 39 Exciter Perturbation Frequency Verification
0.65 Hz
0.7 Hz
0.75 Hz
Gen_MW

## Slide 17: Gen 39 Exciter Perturbation Frequency Verification
0.65 Hz
0.7 Hz
0.75 Hz
Gen_Efd

## Slide 18: Gen 39 Exciter Frequency Verification Full Results
Solar Gen

## Slide 19: Gen 39 Exciter Frequency Verification Full Results

## Slide 20: Gen 39 Exciter Frequency Verification Full Results

## Slide 21: Gen 39 Exciter Frequency Verification Full Results

## Slide 22: Gen 39 Exciter Frequency Verification Full Results

## Slide 23: Gen 39 Exciter Frequency Verification Full Results

## Slide 24: Gen 39 Load Perturbation Frequency Sweep
Perturb load at bus 39 by +/- 200 MW rectangular pulse
Perturbation frequencies:
  0.4 Hz
  0.5 Hz
  0.6 Hz
  0.7 Hz
  0.8 Hz
Contingency: Gen 39 Load Frequency Sweep

## Slide 25: Gen 39 Load Perturbation Frequency Sweep
0.4 Hz
0.5 Hz
0.6 Hz
0.7 Hz
0.8 Hz
Gen_MW

## Slide 26: Gen 39 Load Perturbation Frequency Sweep
0.4 Hz
0.5 Hz
0.6 Hz
0.7 Hz
0.8 Hz
Gen_Efd

## Slide 27: Gen 39 Load Frequency Sweep Full Result

## Slide 28: Gen 39 Load Frequency Sweep Full Result

## Slide 29: Gen 39 Load Frequency Sweep Full Result

## Slide 30: Gen 39 Load Frequency Sweep Full Result

## Slide 31: Gen 39 Load Frequency Sweep Full Result

## Slide 32: Gen 39 Load Frequency Sweep Full Result

## Slide 33: Gen 39 Load Frequency Sweep Full Result

## Slide 34: Non-rectangular Load Pulse Shapes
Most likely due to how Power World does it transient/dynamic computation
Changing the parameters and active/inactive of Power Worlds WSCC transient stability load model does change the output load. However, varying the parameters still does not produce a rectangular pulse.
Default parameters and originally set as inactive

## Slide 35: Gen 39 Load Perturbation Frequency Verification
Scan resulted in a resonance frequency around ~0.7 Hz
Perturb system with frequency 0.7 +/- 0.05 Hz
Perturbation frequencies:
  0.65 Hz
  0.70 Hz
  0.75 Hz

## Slide 36: Gen 39 Load Perturbation Frequency Verification
0.65 Hz
0.7 Hz
0.75 Hz
Gen_MW

## Slide 37: Gen 39 Load Perturbation Frequency Verification
0.65 Hz
0.7 Hz
0.75 Hz
Gen_Efd

## Slide 38: Gen 39 Load Frequency Verification Full Results

## Slide 39: Gen 39 Load Frequency Verification Full Results

## Slide 40: Gen 39 Load Frequency Verification Full Results

## Slide 41: Gen 39 Load Frequency Verification Full Results

## Slide 42: Gen 39 Load Frequency Verification Full Results

## Slide 43: Gen 39 Load Frequency Verification Full Results

## Slide 44: Gen 37 Exciter Setpoint Frequency Sweep
Perturb exciter setpoint by +/- 5% rectangular pulse of starting setpoint
Perturbation frequencies:
  1.4 Hz
  1.5 Hz
  1.6 Hz
  1.7 Hz
  1.8 Hz
  1.9 Hz
Contingency: Gen 37 Efd Frequency Sweep

## Slide 45: Gen 37 Exciter Setpoint Frequency Sweep
1.4 Hz
1.5 Hz
1.6 Hz
1.7 Hz
1.8 Hz
1.9 Hz

## Slide 46: Gen 37 Exciter Setpoint Frequency Sweep
1.4 Hz
1.5 Hz
1.6 Hz
1.7 Hz
1.8 Hz
1.9 Hz

## Slide 47: Gen 37 Exciter Frequency Sweep Full Result

## Slide 48: Gen 37 Exciter Frequency Sweep Full Result

## Slide 49: Gen 37 Exciter Frequency Sweep Full Result

## Slide 50: Gen 37 Exciter Frequency Sweep Full Result

## Slide 51: Gen 37 Exciter Frequency Sweep Full Result

## Slide 52: Gen 37 Exciter Frequency Sweep Full Result

## Slide 53: Gen 37 Exciter Perturbation Frequency Verification
Scan resulted in a resonance frequency between 1.7 – 1.8 Hz
Perturb system with frequency 1.75 +/- 0.05 Hz
Perturbation frequencies:
  1.70 Hz
  1.75 Hz
  1.80 Hz
Contingency: Gen 37 Efd Frequency Verification

## Slide 54: Gen 37 Exciter Perturbation Frequency Verification
Gen_MW
1.7 Hz
1.75 Hz
1.8 Hz

## Slide 55: Gen 37 Exciter Perturbation Frequency Verification
Gen_Efd
1.7 Hz
1.75 Hz
1.8 Hz

## Slide 56: Gen 37 Exciter Frequency Verification Full Result

## Slide 57: Gen 37 Exciter Frequency Verification Full Result

## Slide 58: Gen 37 Exciter Frequency Verification Full Result

## Slide 59: Gen 37 Exciter Frequency Verification Full Result

## Slide 60: Gen 37 Exciter Frequency Verification Full Result

## Slide 61: Gen 37 Exciter Frequency Verification Full Result

## Slide 62: Gen 37 Load Frequency Sweep
Perturb load 25 by +/- 200 MW rectangular pulse
Perturbation frequencies:
  1.4 Hz
  1.5 Hz
  1.6 Hz
  1.7 Hz
  1.8 Hz
  1.9 Hz

## Slide 63: Gen 37 Load Frequency Sweep
Gen_MW
1.4 Hz
1.5 Hz
1.6 Hz
1.7 Hz
1.8 Hz
1.9 Hz

## Slide 64: Gen 37 Load Frequency Sweep
Gen_Efd
1.4 Hz
1.5 Hz
1.6 Hz
1.7 Hz
1.8 Hz
1.9 Hz

## Slide 65: Gen 37 Load Frequency Sweep Full Result

## Slide 66: Gen 37 Load Frequency Sweep Full Result

## Slide 67: Gen 37 Load Frequency Sweep Full Result

## Slide 68: Gen 37 Load Frequency Sweep Full Result

## Slide 69: Gen 37 Load Frequency Sweep Full Result

## Slide 70: Gen 37 Load Frequency Sweep Full Result

## Slide 71: Gen 37 Load Frequency Sweep Full Result

## Slide 72: Gen 37 Load Perturbation Frequency Verification
Scan resulted in a resonance frequency between 1.7 – 1.8 Hz
Perturb system with frequency 1.75 +/- 0.05 Hz
Perturbation frequencies:
  1.70 Hz
  1.75 Hz
  1.80 Hz
Contingency: Gen 37 Load Frequency Verification

## Slide 73: Gen 37 Load Perturbation Frequency Verification
Gen_MW
1.7 Hz
1.75 Hz
1.8 Hz

## Slide 74: Gen 37 Load Perturbation Frequency Verification
Gen_Efd
1.7 Hz
1.75 Hz
1.8 Hz

## Slide 75: Gen 37 Load Frequency Verification Full Result

## Slide 76: Gen 37 Load Frequency Verification Full Result

## Slide 77: Gen 37 Load Frequency Verification Full Result

## Slide 78: Gen 37 Load Frequency Verification Full Result

## Slide 79: Gen 37 Load Frequency Verification Full Result

## Slide 80: Gen 37 Load Frequency Verification Full Result

## Slide 81: Gen 37 Load Frequency Verification Full Result

## Slide 82: Gen 30 Exciter Setpoint Frequency Sweep
Perturb exciter setpoint by +/- 5% rectangular pulse of starting setpoint
Perturbation frequencies:
  1 Hz
  1.1 Hz
  1.2 Hz
  1.3 Hz
  1.4 Hz
Contingency: Gen 30 Efd Frequency Sweep

## Slide 83: Gen 30 Exciter Setpoint Frequency Sweep
1 Hz
1.1 Hz
1.2 Hz
1.3 Hz
1.4 Hz
Gen_MW

## Slide 84: Gen 30 Exciter Setpoint Frequency Sweep
1 Hz
1.1 Hz
1.2 Hz
1.3 Hz
1.4 Hz
Gen_Efd

## Slide 85: Gen 30 Exciter Frequency Sweep Full Results

## Slide 86: Gen 30 Exciter Frequency Sweep Full Results

## Slide 87: Gen 30 Exciter Frequency Sweep Full Results

## Slide 88: Gen 30 Exciter Frequency Sweep Full Results

## Slide 89: Gen 30 Exciter Frequency Sweep Full Results

## Slide 90: Gen 30 Exciter Frequency Sweep Full Results

## Slide 91: Gen 30 Exciter Frequency Verification
Scan resulted in a resonance frequency around ~1.2 Hz
Perturb system with frequency 1.2 +/- 0.05 Hz
Perturbation frequencies:
  1.15 Hz
  1.20 Hz
  1.25 Hz
Contingency: Gen 30 Efd Frequency Verification

## Slide 92: Gen 30 Exciter Frequency Verification
1.15 Hz
1.2 Hz
1.25 Hz
Gen_MW

## Slide 93: Gen 30 Exciter Frequency Verification
1.15 Hz
1.2 Hz
1.25 Hz
Gen_Efd

## Slide 94: Gen 30 Exciter Frequency Verification Full Result

## Slide 95: Gen 30 Exciter Frequency Verification Full Result

## Slide 96: Gen 30 Exciter Frequency Verification Full Result

## Slide 97: Gen 30 Exciter Frequency Verification Full Result

## Slide 98: Gen 30 Exciter Frequency Verification Full Result

## Slide 99: Gen 30 Exciter Frequency Verification Full Result

## Slide 100: Gen 30 Load Frequency Sweep
Perturb load 25 by +/- 200 MW rectangular pulse
Perturbation frequencies:
  1 Hz
  1.1 Hz
  1.2 Hz
  1.3 Hz
  1.4 Hz
Contingency: Gen 30 Load Frequency Sweep

## Slide 101: Gen 30 Load Frequency Sweep
Gen_MW
1 Hz
1.1 Hz
1.2 Hz
1.3 Hz
1.4 Hz

## Slide 102: Gen 30 Load Frequency Sweep
Gen_Efd
1 Hz
1.1 Hz
1.2 Hz
1.3 Hz
1.4 Hz

## Slide 103: Gen 30 Load Frequency Sweep Full Result

## Slide 104: Gen 30 Load Frequency Sweep Full Result

## Slide 105: Gen 30 Load Frequency Sweep Full Result

## Slide 106: Gen 30 Load Frequency Sweep Full Result

## Slide 107: Gen 30 Load Frequency Sweep Full Result

## Slide 108: Gen 30 Load Frequency Sweep Full Result

## Slide 109: Gen 30 Load Frequency Sweep Full Result

## Slide 110: Gen 30 Load Frequency Verification
Scan resulted in a resonance frequency around ~1.2 Hz
Perturb system with frequency 1.2 +/- 0.05 Hz
Perturbation frequencies:
  1.15 Hz
  1.20 Hz
  1.25 Hz
Contingency: Gen 30 Load Frequency Verification

## Slide 111: Gen 30 Load Frequency Verification
1.15 Hz
1.2 Hz
1.25 Hz
Gen_MW

## Slide 112: Gen 30 Load Frequency Verification
1.15 Hz
1.2 Hz
1.25 Hz
Gen_Efd

## Slide 113: Gen 30 Load Frequency Verification Full Results

## Slide 114: Gen 30 Load Frequency Verification Full Results

## Slide 115: Gen 30 Load Frequency Verification Full Results

## Slide 116: Gen 30 Load Frequency Verification Full Results

## Slide 117: Gen 30 Load Frequency Verification Full Results

## Slide 118: Gen 30 Load Frequency Verification Full Results

## Slide 119: Appendix A: Power World SMIB Eigenvalues

## Slide 120: Appendix A: Power World SMIB Eigenvalues

## Slide 121: Appendix A: Power World SMIB Eigenvalues

## Slide 122: Appendix A: Power World SMIB Eigenvalues

## Slide 123: Appendix A: Power World SMIB Eigenvalues

## Slide 124: Appendix B: System Mode (PW and PST)
 | Power World SMIB |  | PST (DC1 Exciter Model) |  | PST (Type 0 Exciter Model) |  | Power World FO Freq Scan
Generator | Damping | Freq Hz | Damping | Freq Hz | Damping | Freq Hz | 
30 | 0.1015 | 1.1642 | 0.056409442 | 1.153905871 | 0.125313448 | 1.16838607 | 
31 | 0.1676 | 1.2601 | 0.043000306 | 1.038776929 | 0.196388567 | 1.175012527 | 
32 | 0.1844 | 1.3751 | 0.037950439 | 1.237107135 | 0.152493802 | 1.404732142 | 
33 | 0.1443 | 1.6165 | 0.051315888 | 1.399023004 | 0.120573128 | 1.504390767 | 
34 | 0.262 | 1.0722 | No lightly damped freq associated with Gen 34 |  | 0.225951469 | 1.076922038 | 
35 | 0.2139 | 1.3375 | 0.050567433 | 1.13118085 | No lightly damped freq associated with Gen 35 |  | 
36 | 0.2969 | 1.3198 | 0.056754348 | 1.459699253 | 0.254468125 | 1.511950024 | 
37 | 0.1894 | 1.7445 | 0.058924133 | 1.468813003 | 0.177674914 | 1.765580528 | 1.7 – 1.8
38 | 0.2606 | 1.2586 | 0.040691254 | 0.987041172 | 0.240917221 | 1.21890335 | 
39 | 0.1589 | 0.406 | 0.041773826 | 0.379150343 | 0.135914054 | 0.598678949 | ~ 0.6
 |  |  | 0.086092542 | 0.639953118 |  |  | 
Note PW SMIB: Picked freq with smallest damping ratio
Note PST: Gen associated with lowest damped frequency was chosen as the gen with normalized participation factor of 1